TDD Access: Relay NH 1-800-735-2964

ARSON HOTLINE 1-800-400-3526

STATE OF NEW HAMPSHIRE DEPARTMENT OF SAFETY

John J. Barthelmes, Commissioner

Division of Fire Safety

Office of the State Fire Marshal

J. William Degnan, State Fire Marshal

Office: 110 Smokey Bear Boulevard, Concord, NH

Mailing Address: 33 Hazen Drive, Concord, N.H. 03305

603-223-4289, FAX 603-223-4295

INFORMATIONAL BULLETIN

ON

RESIDENTIAL GENERATOR SAFETY

(REVISED) JUNE 22, 2009

The State Fire Marshal has developed this informational document to provide

homeowners and other residents of New Hampshire with valuable information about

generator safety during periods of power outages. Accidental fires from improper

refueling methods, improper wiring methods, and carbon monoxide poisoning from

exhaust can cause severe injuries or death to citizens. In addition, linemen attempting

to restore power to the area can be injured or killed if the generator is not installed

properly. For additional safety inspections and tips please contact your local Fire

Department or this office at (603) 223-4289 or fmo@dos.nh.gov .

Portable Generators

Portable generators should be placed 10 feet from any structure, with the exhaust

facing away from the building openings. Deadly exhaust fumes can enter the building

through any opening resulting in severe injury or death to unsuspecting occupants.

Never place portable generators on or near combustible surfaces such as decks,

porches, or tool sheds. Heat generated by the motor, or improper refueling methods can

start a fire.

Never run portable generators inside any building, including basement areas and

garages. Deadly levels of carbon monoxide can build up in minutes injuring occupants

with little to no warning.

Allow plenty of time to cool the generator before refueling. Gasoline vapors can easily

ignite from hot surfaces causing a flash fire and severe injuries.

Always store approved gasoline containers a safe distance from generators while in

use. Always store gasoline in an approved container placed in a well ventilated storage

area. Never store gasoline products in basements or enclosed areas of your dwelling.

Generator Safety Informational Bulletin

June 22, 2009

Page 2

Never modify or construct any power cord so a generator can be connected to a

receptacle, dryer or range outlet.

Never connect a generator directly to panelboard without a means to prevent

inadvertent connection to the normal supply system wiring. Connecting a generator

directly to an electrical outlet or to a panelboard without a transfer switch or an

interlocking device could result in a situation where power from the generator could

energize the utility’s wiring (back feeds into the utility system). Electrical power from a

generator back fed through your meter into the utility system can cause fires, serious

injury or death to utility workers trying to repair the lines in the street, or electricians

working on nearby property’s electrical systems.

Unless you are the owner of, and are occupying, a single family residence or meet one

of the exceptions in RSA 319-C, a license is required to perform the electrical

installation for connection of a generator to premises wiring. Therefore, a properly

licensed master electrician must perform the electrical installation. In all cases the

electrical installation must meet the minimum requirements of the National Electrical

Code (NFPA 70-2008).

Although the generator is portable, an electrical permit and inspection may be required

by the local jurisdiction for the installation of electrical wiring and equipment for

connecting the generator to the premises wiring. Therefore it would be prudent to

contact the local jurisdiction to ascertain whether an electrical permit is required.

Stationary Generator Installations

In many cases property owners have chosen to install a stationary generator. In

addition to the above mentioned items, stationary generators used for an alternate

source of power require additional considerations. Along with the National Electrical

Code (NFPA 70-2008) the requirements of other documents, that are either adopted

directly or by reference by the State of New Hampshire, must be adhered to. Examples

of these documents and the types of requirements they contain are:

NFPA 37, Standard for the Installation and Use of Stationary Combustion

Engines and Gas Turbines (2002 Edition)

NFPA 54, National Fuel Gas Code (2003 Edition)

The Manufacturers Instructions

NFPA 37 requires stationary generator engines and their weatherproof housings if

provided, that are installed outdoors to be located at least 5’ from openings in walls.

This standard recognizes the potential danger of deadly carbon monoxide gas entering

the structure and injuring the occupants. Building openings could be, but are not limited

to, the following:

Generator Safety Informational Bulletin

June 22, 2009

Page 3

Basement doors & bulkhead openings

Basement windows

Exit doors or sliding glass openings

Windows

Dryer vents

Kitchen appliance vents

Mechanical exhaust vents for heating or hot water appliances

Air intake openings or screens

NFPA 37 also requires stationary generator engines and their weatherproof housings, if

provided, that are installed outdoors to be placed a minimum of five feet (5’) from

structures having combustible walls. The minimum separation is not required where:

(1) The adjacent wall of the structure has a fire resistance rating of at least 1 hour or

(2) The weatherproof enclosure is constructed of noncombustible materials, which

has been listed and approved in accordance with NFPA 555, verifying that a fire

within the enclosure will not ignite combustible materials outside the enclosure.

These allowances apply directly to the separation from the combustible wall surface and

in no case shall reduce the minimum distance to a building opening.

The fuel gas piping must be installed in accordance with both NFPA 37 and NFPA 54

(National Fuel Gas Code). These documents require that the second stage system

regulator be placed a minimum of five feet (5’) from any building opening and ignition

source. Care must be given in placement of both the generator engine and delivery

system piping to address the minimum separation distances.

Unless you are the owner of, and are occupying, a single family residence or meet one

of the exceptions in RSA 319-C, a license is required to perform the electrical

installation for connection of a stationary generator to premises wiring. Therefore, a

properly licensed master electrician must perform the electrical installation. In all cases

the electrical installation must meet the minimum requirements of the National Electrical

Code (NFPA 70-2008).

Unless you are the owner of an existing single family stand-alone structure that is used

as your primary residence, Saf-C 8003.01 requires a license to perform the installation

of the fuel gas supply system. In all cases the installation of the fuel gas supply system

must meet all the applicable standards and codes.

Installation permits and inspection may be required by the local jurisdiction for the

installation of electrical wiring and equipment for connecting the generator to the

premises wiring and for the fuel gas fitting portion of the installation. Therefore it would

be prudent to contact the local jurisdiction to ascertain whether a permit(s) is required.

Generator Safety Informational Bulletin

June 22, 2009

Page 4